## Index & Summary
Checklist_ID | Tab_Name | Domain / Category | Checklist_Title | Standard_Basis | Items_Count | Application_Notes
CHK-SAFETY-70E | NFPA 70E Safety | SAFETY | NFPA 70E Pre-Work Hazard Analysis & Safety | NFPA 70E Standard for Electrical Safety in the Workplace | 4 | Used for safety inspection and code verification.
CHK-GEN-110 | NEC 110 Clearances | GENERAL | General Working Clearances & Enclosure Environment | NEC 2023 / NFPA 70 Article 110 (General Requirements) | 6 | Used for general inspection and code verification.
CHK-PANEL-408 | NEC 408 Panels & Gear | PANEL | Panelboards, Switchboards & Switchgear Audit | NEC Article 408 & NFPA 70B (Panelboards & Switchboards) | 5 | Used for panel inspection and code verification.
CHK-XFRM-450 | NEC 450 Transformers | TRANSFORMER | Dry-Type & Liquid Transformers Verification | NEC Article 450 & NFPA 70B (Transformers) | 4 | Used for transformer inspection and code verification.
CHK-BKR-240 | NEC 240 Breakers & Fuses | BREAKER | Circuit Breakers & Fuses Verification | NEC Article 240 & NFPA 70B (Overcurrent Protection) | 3 | Used for breaker inspection and code verification.
CHK-GND-250 | NEC 250 Grounding | GROUNDING | Grounding Electrode System & Equipment Bonding | NEC Article 250 (Grounding & Bonding) | 3 | Used for grounding inspection and code verification.
CHK-SW-404 | NEC 404 Switches & Motors | SWITCH | Disconnect Switches & Motor Controls | NEC Article 404 & 430 (Switches & Motors) | 3 | Used for switch inspection and code verification.

## NFPA 70E Safety
Item_No | Standard_Ref | Inspection_Prompt | Verification_Criteria | Severity | Standard_Frequency | Guidance_Notes | Checklist_ID | Category | Checklist_Title
1 | NFPA 70E 110.1 | Verify electrical safety program and site job safety briefing. | Job safety plan documented and briefing conducted with all personnel before opening equipment. | Critical | Pre-Task | Mandatory before opening any energized electrical enclosure. | CHK-SAFETY-70E | safety | NFPA 70E Pre-Work Hazard Analysis & Safety
2 | NFPA 70E 130.5 | Verify equipment has an updated Arc Flash risk assessment & label. | Label displays nominal system voltage, arc flash boundary, and incident energy (cal/cm2) or PPE category. | Critical | Visual / Initial | Labels must be updated whenever system modifications occur or at minimum every 5 years. | CHK-SAFETY-70E | safety | NFPA 70E Pre-Work Hazard Analysis & Safety
3 | NFPA 70E 130.4 | Establish shock protection boundaries (Limited and Restricted approach). | Boundaries clearly identified based on system AC/DC voltage tables. | Critical | Pre-Task | Only qualified persons with appropriate insulated tools permitted inside restricted boundary. | CHK-SAFETY-70E | safety | NFPA 70E Pre-Work Hazard Analysis & Safety
4 | NFPA 70E 130.7 | Inspect PPE condition and voltage ratings for task. | Rubber insulating gloves air-tested and within test date; arc-rated face shield/suit clean and undamaged. | Critical | Pre-Task | Rubber insulating gloves must be electrically re-tested every 6 months. | CHK-SAFETY-70E | safety | NFPA 70E Pre-Work Hazard Analysis & Safety

## NEC 110 Clearances
Item_No | Standard_Ref | Inspection_Prompt | Verification_Criteria | Severity | Standard_Frequency | Guidance_Notes | Checklist_ID | Category | Checklist_Title
1 | NEC 110.26(A)(1) | Verify minimum 36-inch (or depth by voltage condition) clear working space in front of equipment. | Unobstructed depth (36 in. up to 150V, 42 in. 151-600V Condition 2) maintaining full 90-degree door swing. | Critical | Initial Survey | Working space cannot be used for permanent or temporary storage. | CHK-GEN-110 | general | General Working Clearances & Enclosure Environment
2 | NEC 110.26(A)(2) | Verify minimum width of working space is at least 30 inches or width of equipment. | Width accommodates equipment footprint and allows unimpeded egress. | Major | Initial Survey | Measure from outer edges of enclosure trim. | CHK-GEN-110 | general | General Working Clearances & Enclosure Environment
3 | NEC 110.26(A)(3) | Verify minimum 6.5 ft (or equipment height) headroom in working space. | Ceiling, piping, and ductwork clear above working area. | Major | Initial Survey | Exceptions apply for existing residential service replacements. | CHK-GEN-110 | general | General Working Clearances & Enclosure Environment
4 | NEC 110.26(E) | Verify dedicated electrical space above and below panelboard/switchboard. | No foreign systems (plumbing, drainage, steam, HVAC ducts) within dedicated zone extending to structural ceiling. | Critical | Initial Survey | Protection against leaks and condensation required if foreign systems pass outside zone. | CHK-GEN-110 | general | General Working Clearances & Enclosure Environment
5 | NEC 110.16(A) | Verify presence of field or factory Arc Flash warning label. | Clearly visible label on switchboards, switchgear, panelboards, and motor control centers. | High | Initial Survey | Required on equipment likely to require examination, adjustment, or maintenance while energized. | CHK-GEN-110 | general | General Working Clearances & Enclosure Environment
6 | NEC 110.28 | Verify enclosure NEMA/IP rating is suitable for environmental conditions. | NEMA 1 (indoor dry), NEMA 3R (outdoor rain), NEMA 4/4X (washdown/corrosive), NEMA 12 (industrial dust/oil). | Major | Initial Survey | Inspect for moisture intrusion, corrosion, or compromised gaskets. | CHK-GEN-110 | general | General Working Clearances & Enclosure Environment

## NEC 408 Panels & Gear
Item_No | Standard_Ref | Inspection_Prompt | Verification_Criteria | Severity | Standard_Frequency | Guidance_Notes | Checklist_ID | Category | Checklist_Title
1 | NEC 408.4(A) | Verify circuit directory / panel schedule is complete, accurate, and legible. | Every circuit breaker clearly identified with specific room/load served; no vague labels like 'Lights'. | Major | Annual / Survey | Crucial for emergency isolation and single-line diagram validation. | CHK-PANEL-408 | panel | Panelboards, Switchboards & Switchgear Audit
2 | NEC 408.36 | Verify panelboard overcurrent protection rating does not exceed busbar rating. | Main breaker or upstream feeder overcurrent device <= panel ampacity rating. | Critical | Initial Survey | Check nameplate continuous current rating against supply device. | CHK-PANEL-408 | panel | Panelboards, Switchboards & Switchgear Audit
3 | NEC 408.41 | Verify grounded conductor (neutral) terminals have only one conductor per terminal. | Each neutral wire connected to an individual terminal screw unless identified for multiple conductors. | Major | Initial Survey | Do not double-lug neutrals on standard terminal bars. | CHK-PANEL-408 | panel | Panelboards, Switchboards & Switchgear Audit
4 | NEC 408.7 | Verify all unused breaker openings are closed with approved filler plates. | No open knockouts or exposed busbar slots on dead-front cover. | High | Visual / Monthly | Prevents accidental finger contact and containment of internal flash. | CHK-PANEL-408 | panel | Panelboards, Switchboards & Switchgear Audit
5 | NFPA 70B 13.2 | Inspect enclosure and busbar for thermal discoloration, arcing, or foreign contamination. | No signs of heat damage, carbon deposits, rodent intrusion, metal shavings, or moisture. | Critical | Annual 70B | Infrared thermography scan recommended under load. | CHK-PANEL-408 | panel | Panelboards, Switchboards & Switchgear Audit

## NEC 450 Transformers
Item_No | Standard_Ref | Inspection_Prompt | Verification_Criteria | Severity | Standard_Frequency | Guidance_Notes | Checklist_ID | Category | Checklist_Title
1 | NEC 450.9 | Verify adequate ventilation clearances around transformer enclosure. | Minimum manufacturer clearance (typically 6-12 inches) maintained from walls and obstructions. | Critical | Initial Survey | Ventilation louvers must be clean and unblocked to prevent thermal degradation. | CHK-XFRM-450 | transformer | Dry-Type & Liquid Transformers Verification
2 | NEC 450.3 | Verify primary and secondary overcurrent protection complies with sizing tables. | Overcurrent device size <= maximum percentage in NEC Table 450.3(A)/(B) (e.g. 125% or next standard size). | Critical | Initial Survey | Calculated based on primary/secondary full-load amperes (FLA). | CHK-XFRM-450 | transformer | Dry-Type & Liquid Transformers Verification
3 | NEC 250.30(A) | Verify separately derived system grounding electrode conductor (GEC) & bonding jumper. | System bonding jumper connects X0 neutral to transformer enclosure and grounding electrode conductor. | Critical | Initial Survey | Sized according to NEC Table 250.102(C)(1) based on derived phase conductors. | CHK-XFRM-450 | transformer | Dry-Type & Liquid Transformers Verification
4 | NFPA 70B 21.2 | Inspect core, coils, and terminal connections for loose lugs, dust buildup, or acoustic noise. | Connections torqued to specification; no abnormal humming, vibration, or insulation varnish cracking. | Major | Annual 70B | Clean coils with dry, low-pressure compressed air or vacuum. | CHK-XFRM-450 | transformer | Dry-Type & Liquid Transformers Verification

## NEC 240 Breakers & Fuses
Item_No | Standard_Ref | Inspection_Prompt | Verification_Criteria | Severity | Standard_Frequency | Guidance_Notes | Checklist_ID | Category | Checklist_Title
1 | NEC 240.4 | Verify conductor ampacity is properly protected by the upstream breaker or fuse rating. | Conductor gauge (AWG/kcmil) ampacity (75°C column) >= overcurrent protective device rating (with standard size rules). | Critical | Initial Survey | Check continuous load factors (125%) where applicable. | CHK-BKR-240 | breaker | Circuit Breakers & Fuses Verification
2 | NEC 240.86 | Verify series ratings or fully rated AIC exceeds available fault current (SCCR). | Interrupting rating (kAIC) of breaker >= available short-circuit current from upstream utility/source. | Critical | Initial Survey | Prevents catastrophic breaker explosion during dead short-circuit. | CHK-BKR-240 | breaker | Circuit Breakers & Fuses Verification
3 | NFPA 70B 17.2 | Exercise molded-case circuit breaker mechanisms and verify smooth handle operation. | Breaker trips and resets crisply; handle not loose or binding. | Major | Annual 70B | De-energized mechanical exercise prevents contact welding. | CHK-BKR-240 | breaker | Circuit Breakers & Fuses Verification

## NEC 250 Grounding
Item_No | Standard_Ref | Inspection_Prompt | Verification_Criteria | Severity | Standard_Frequency | Guidance_Notes | Checklist_ID | Category | Checklist_Title
1 | NEC 250.50 | Verify all available grounding electrodes (water pipe, steel frame, rod/pipe, concrete-encased) bonded together. | Interconnected into a single Grounding Electrode System (GES). | Critical | Initial Survey | 25 ohms or supplemental electrode required for single rod/pipe/plate. | CHK-GND-250 | grounding | Grounding Electrode System & Equipment Bonding
2 | NEC 250.64(E) | Verify bonding of ferrous metal raceways containing Grounding Electrode Conductors (GEC). | Both ends of conduit bonded to ensure low-impedance path and eliminate inductive choke effect. | Critical | Initial Survey | Bonding bushings required at both service enclosure and electrode entry. | CHK-GND-250 | grounding | Grounding Electrode System & Equipment Bonding
3 | NEC 250.122 | Verify equipment grounding conductor (EGC) size in raceway/cable matches upstream overcurrent device. | Sized per Table 250.122 (e.g. 10 AWG Cu for 30A, 8 AWG for 40/50A, 6 AWG for 60A). | Critical | Initial Survey | Must be increased proportionally if ungrounded conductors are upsized for voltage drop. | CHK-GND-250 | grounding | Grounding Electrode System & Equipment Bonding

## NEC 404 Switches & Motors
Item_No | Standard_Ref | Inspection_Prompt | Verification_Criteria | Severity | Standard_Frequency | Guidance_Notes | Checklist_ID | Category | Checklist_Title
1 | NEC 430.102 | Verify disconnect switch is in sight from motor location (or lockable in open position). | Within 50 ft and visible line of sight unless locked under safety protocol. | Critical | Initial Survey | Disconnect must open all ungrounded supply conductors simultaneously. | CHK-SW-404 | switch | Disconnect Switches & Motor Controls
2 | NEC 404.6(A) | Verify knife switches / safety switches are installed so gravity will not close them. | Up position = ON / Closed; Down position = OFF / Open. | Critical | Initial Survey | Enclosure interlock prevents opening door with switch in ON position. | CHK-SW-404 | switch | Disconnect Switches & Motor Controls
3 | NFPA 70B 16.2 | Inspect switch blade contacts for pitting, burning, alignment, and spring tension. | Clean contact surface; adequate clip pressure and uniform blade engagement. | Major | Annual 70B | Check fuse clip tension and apply dielectric lubricant if specified. | CHK-SW-404 | switch | Disconnect Switches & Motor Controls